| Water System Name: | COMMUNITY CHRISTIAN SCHOOL | Report Date: | June 2014 |
| --- | --- | --- | --- |

We test the drinking water quality for many constituents as required by state and federal regulations. This report shows the results of our monitoring for the period of January 1 - December 31, 2013

Este informe contiene información muy importante sobre su agua beber. Tradúzcalo ó hable con alguien que lo entienda bien.

Type of water sources(s) in use:  According to CDPH records, this Source is Groundwater. This Assessment was done using the Default Groundwater System Method.

Your water comes from 1 source:  Well #1.

For more information about this report, or for any questions relating to your drinking water, please call (805) 967-2671 Ext. 111 and ask for Bob Strojek, or visit our website at www.comcov.com

| TERMS USED IN THIS REPORT: |
| --- |
| Maximum Contaminant Level (MCL): The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water. Maximum Contaminant Level Goal (MCLG): The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the U.S. Environmental Protection Agency. Public Health Goal (PHG): The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency. Maximum Residual Disinfectant Level (MRDL): The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants. Maximum Residual Disinfectant Level Goal (MRDLG): The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants. | Primary Drinking Water Standards (PDWS): MCLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. Secondary Drinking Water Standards (SDWS): MCLs for contaminants that affect taste, order, or appearance of the drinking water. Contaminants with SDWSs do not affect the health at the MCL levels. Regulatory Action Level (AL): The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow. Variances and Exemptions: Department permission to exceed an MCL or not comply with a treatment technique under certain conditions. ND: not detectable at testing limit ppm: parts per million or milligrams per liter (mg/L) ppb: parts per billion or micrograms per liter (µg/L) umhos/cm: micromhos per centimeter (a measure of conductivity) TON: threshold odor numbers (a measure of odor) pCi/l: picocuries per liter (a measure of radioactivity) |

The sources of drinking water(both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, spring, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in source water include:

- Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations and wildlife.

- Inorganic contaminants, such as salts and metals, which can be naturally-occurring or result from urban stormwater runoff, industrial or domestic wastewater discharges, oil and gas production, mining or farming.

- Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.

- Radioactive contaminants, which can be naturally occurring or the result of oil production and mining activities.

- Organic chemical contaminants, including synthetic and volatile organic chemicals, which are byproducts of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, and septic systems.

In order to ensure that tap water is safe to drink,  the U.S. Environmental Protection Agency (USEPA) and the California Department of Public Health  prescribes regulations which limit the amount of certain contaminants in water provided by public water systems.  Department regulations also establish limits for contaminants in bottled water that must provide the same protection for public health.

Tables 1 and 2 list all of the drinking water contaminants that were detected during the most recent sampling for the constituents.  The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. The Department allows us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not change frequently. Some of the data, though representative of the water quality, are more than one year old.

| Table 1 - Sampling Results showing the detection of Lead and Copper |
| --- |
| Lead and Copper (complete if lead or copper detected in the last sample set) | No. of Samples Collected | 90th Percentile Level | No. Site Exceeding AL | AL | PHG | Typical Sources of Contaminant |
| Lead (ppb) | 5 (2013) | 4.25 | 0 | 15 | 0.2 | Internal corrosion of household water plumbing systems; discharges from industrial manufacturers, erosion of natural deposits |
| Copper (ppm) | 5 (2013) | 1.065 | 1 | 1.3 | .3 | Internal corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |

| Table 2 - Detection of Contaminants with a Primary Drinking Water Standard |
| --- |
| Chemical or Constituent | Sample | Level | Range of | MCL | PHG |  |
| (and reporting units) | Date | Detected | Detections | (MRDL) | (MCLG) [MRDLG] | Typical Sources of Contaminant |
| Nitrate (ppm) | (2013) | 3.70 | 3.70 – 3.70 | 45 | 45 | Runoff and leaching from fertilizer use; leaching from septic tanks and sewage; erosion of natural deposits |
| Gross Alpha (pCi/L) | (2010 - 2011) | 4.2 | 3 - 5 | 15 | (0) | Erosion of natural deposits. |
| Uranium (pCi/L) | (2010 - 2011) | 3.2 | 2 - 4 | 20 | 0.43 | Erosion of natural deposits |

Additional General Information on Drinking Water

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the USEPA`s Safe Drinking Water Hotline (800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care provider. USEPA/Centers for Disease Control (CDC) guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (800-426-4791)

For Lead (Pb),  If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children.  Lead in drinking water is primarily from materials and components associated with service lines and home plumbing.  COMMUNITY CHRISTIAN SCHOOL  is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components.  When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking.  If you are concerned about lead in your water, you may wish to have your water tested.  Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline or at  http://www.epa.gov/safewater/lead.

Drinking Water Source Assessment Information

Assessment Info

A source water assessment was conducted for the WELL #1 of the COMMUNITY CHRISTIAN SCHOOL water system in August, 2002.

Discussion of Vulnerability

The source is not considered vulnerable to any potentially contaminating activities at this time.

Acquiring Info

A copy of the complete assessment may be viewed at:

Environmental Health Services

225 Camino del Remedio

Santa Barbara, CA 93110

You may request a summary of the assessment be sent to you by contacting:

Norman Fujimoto

Environmental Health Specialist

805-681-4917

Fujimoto@co.santa-barbara.ca.us